## PressurisationAuto
Modulus of PE |  |  |  | 1st stage filling volume
Temperature (Assume 10°C for buried pipe installations, unless better information exists.) | °C | 10 | Please input (Only temperatures less than or equal to 20°C should be entered in this field) | Pipe Volume | litres | 735.9369
Ramp up time | min | 15 | Please input (Only whole numbers up to and including 30 minutes should be entered in this field.) | Max content of air in litres to deliver a valid test for start pressure: 2 bar absolute | litres | 14.7187
Material Choice | - | PE100 | Please select from dropdown | Minimum volume of water to deliver a valid test. | litres | 721.2182
Modulus of PE As provided by the manufacturer for the temperature above NOTE:If left blank the PE Modulus will be calculated as per the Equations for Modulus | N/m2 |  | Please input if needed as per note
Epe Modulus of PE* (Value to be derived from the equation in Table A.5 or A.6 or from the manufacturer's data.) | N/m2 | 1170600000
2nd stage Pressurisation
Description | Unit | Value |  | Pressurisation Volume (No Air) | litres | 12.726
Pipe external diameter (DN) | mm | 110 | Please select from dropdown | Pressurisation Volume with 2.00% air | litres | 25.4823
SDR | - | 17 | Please select from dropdown
Length | metre | 100 | Please input
Pipe min wall thickness | metres | 0.0066 | Auto calculated ( to be hidden)
Start Pressure | bar (absolute) | 2 | Please input
Max Pressure | bar (absolute) | 15 | Please input
Max air content to deliver a valid test for start pressure: 2 bar absolute |  | 2% | For Information
delta P | Pa | 1300000 | To be hidden
Pipe Radius | metres | 0.055 | To be hidden
Modulus of water | Pa | 2050000000 | To be hidden
Draft

## WallThickness (hidden)
| This the table that the formulas get the wall thickness | [11 empty] | Wall thickness Calculation basde on SDR | [10 empty] | % difference in the wall thickness between 12201 and SDR calculation
| S | 2.5 | 3.2 | 4 | 5 | 6.3 | 8 | 10 | 12.5 | 16 | 20
| SDR | 6 | 7.4 | 9 | 11 | 13.6 | 17 | 21 | 26 | 33 | 41 |  | SDR | 6 | 7.4 | 9 | 11 | 13.6 | 17 | 21 | 26 | 33 | 41 | SDR | 6 | 7.4 | 9 | 11 | 13.6 | 17 | 21 | 26 | 33 | 41
Size in WIS | Diameter | emin | emin | emin | emin | emin | emin | emin | emin | emin | emin |  | Diameter | [10 empty] | Diameter
|  | 6emin | 7.4emin | 9emin | 11emin | 13.6emin | 17emin | 21emin | 26emin | 33emin | 41emin
No | 16 | 3 | 2.3 | 2 | [7 empty] | Helper | 16 | 2.6667 | 2.1622 | 1.7778 | [7 empty] | 16 | 12.5% | 6.375% | 12.5%
No | 20 | 3.4 | 3 | 2.3 | 2 | [6 empty] | PE80 | 20 | 3.3333 | 2.7027 | 2.2222 | 1.8182 | [6 empty] | 20 | 2% | 11% | 3.5% | 10%
No | 25 | 4.2 | 3.5 | 3 | 2.3 | 2 | [5 empty] | PE100 | 25 | 4.1667 | 3.3784 | 2.7778 | 2.2727 | 1.8382 | [5 empty] | 25 | 0.8% | 3.6% | 8% | 1.2% | 8.8%
No | 32 | 5.4 | 4.4 | 3.6 | 3 | 2.4 | 2 |  |  |  |  | Pressurisation Volume with | 32 | 5.3333 | 4.3243 | 3.5556 | 2.9091 | 2.3529 | 1.8824 |  |  |  |  | 32 | 1.25% | 1.75% | 1.25% | 3.125% | 2% | 6.25%
No | 40 | 6.7 | 5.5 | 4.5 | 3.7 | 3 | 2.4 | 2 |  |  |  |  | 40 | 6.6667 | 5.4054 | 4.4444 | 3.6364 | 2.9412 | 2.3529 | 1.9048 |  |  |  | 40 | 0.5% | 1.75% | 1.25% | 1.75% | 2% | 2% | 5%
No | 50 | 8.3 | 6.9 | 5.6 | 4.6 | 3.7 | 3 | 2.4 | 2 |  |  |  | 50 | 8.3333 | 6.7568 | 5.5556 | 4.5455 | 3.6765 | 2.9412 | 2.381 | 1.9231 |  |  | 50 | -0.4% | 2.12% | 0.8% | 1.2% | 0.64% | 2% | 0.8% | 4%
Yes | 63 | 10.5 | 8.6 | 7.1 | 5.8 | 4.7 | 3.8 | 3 | 2.5 |  |  |  | 63 | 10.5 | 8.5135 | 7 | 5.7273 | 4.6324 | 3.7059 | 3 | 2.4231 |  |  | 63 | 0% | 1.016% | 1.429% | 1.27% | 1.46% | 2.54% | 0% | 3.175%
No | 75 | 12.5 | 10.3 | 8.4 | 6.8 | 5.6 | 4.5 | 3.6 | 2.9 |  |  |  | 75 | 12.5 | 10.1351 | 8.3333 | 6.8182 | 5.5147 | 4.4118 | 3.5714 | 2.8846 |  |  | 75 | 0% | 1.627% | 0.8% | -0.2667% | 1.547% | 2% | 0.8% | 0.5333%
Yes | 90 | 15 | 12.3 | 10.1 | 8.2 | 6.7 | 5.4 | 4.3 | 3.5 |  |  |  | 90 | 15 | 12.1622 | 10 | 8.1818 | 6.6176 | 5.2941 | 4.2857 | 3.4615 |  |  | 90 | 0% | 1.133% | 1% | 0.2222% | 1.244% | 2% | 0.3333% | 1.111%
Yes | 110 | 18.3 | 15.1 | 12.3 | 10 | 8.1 | 6.6 | 5.3 | 4.2 |  |  |  | 110 | 18.3333 | 14.8649 | 12.2222 | 10 | 8.0882 | 6.4706 | 5.2381 | 4.2308 |  |  | 110 | -0.1818% | 1.582% | 0.6364% | 0% | 0.1455% | 2% | 1.182% | -0.7273%
Yes | 125 | 20.8 | 17.1 | 14 | 11.4 | 9.2 | 7.4 | 6 | 4.8 |  |  |  | 125 | 20.8333 | 16.8919 | 13.8889 | 11.3636 | 9.1912 | 7.3529 | 5.9524 | 4.8077 |  |  | 125 | -0.16% | 1.232% | 0.8% | 0.32% | 0.096% | 0.64% | 0.8% | -0.16%
No | 140 | 23.3 | 19.2 | 15.7 | 12.7 | 10.3 | 8.3 | 6.7 | 5.4 |  |  |  | 140 | 23.3333 | 18.9189 | 15.5556 | 12.7273 | 10.2941 | 8.2353 | 6.6667 | 5.3846 |  |  | 140 | -0.1429% | 1.486% | 0.9286% | -0.2143% | 0.05714% | 0.7857% | 0.5% | 0.2857%
Yes | 160 | 26.6 | 21.9 | 17.9 | 14.6 | 11.8 | 9.5 | 7.7 | 6.2 |  |  |  | 160 | 26.6667 | 21.6216 | 17.7778 | 14.5455 | 11.7647 | 9.4118 | 7.619 | 6.1538 |  |  | 160 | -0.25% | 1.287% | 0.6875% | 0.375% | 0.3% | 0.9375% | 1.063% | 0.75%
Yes | 180 | 29.9 | 24.6 | 20.1 | 16.4 | 13.3 | 10.7 | 8.6 | 6.9 |  |  |  | 180 | 30 | 24.3243 | 20 | 16.3636 | 13.2353 | 10.5882 | 8.5714 | 6.9231 |  |  | 180 | -0.3333% | 1.133% | 0.5% | 0.2222% | 0.4889% | 1.056% | 0.3333% | -0.3333%
No | 200 | 33.2 | 27.4 | 22.4 | 18.2 | 14.7 | 11.9 | 9.6 | 7.7 |  |  |  | 200 | 33.3333 | 27.027 | 22.2222 | 18.1818 | 14.7059 | 11.7647 | 9.5238 | 7.6923 |  |  | 200 | -0.4% | 1.38% | 0.8% | 0.1% | -0.04% | 1.15% | 0.8% | 0.1%
Yes | 225 | 37.4 | 30.8 | 25.2 | 20.5 | 16.6 | 13.4 | 10.8 | 8.6 |  |  |  | 225 | 37.5 | 30.4054 | 25 | 20.4545 | 16.5441 | 13.2353 | 10.7143 | 8.6538 |  |  | 225 | -0.2667% | 1.298% | 0.8% | 0.2222% | 0.3378% | 1.244% | 0.8% | -0.6222%
Yes | 250 | 41.5 | 34.2 | 27.9 | 22.7 | 18.4 | 14.8 | 11.9 | 9.6 |  |  |  | 250 | 41.6667 | 33.7838 | 27.7778 | 22.7273 | 18.3824 | 14.7059 | 11.9048 | 9.6154 |  |  | 250 | -0.4% | 1.232% | 0.44% | -0.12% | 0.096% | 0.64% | -0.04% | -0.16%
Yes | 280 | 46.5 | 38.3 | 31.3 | 25.4 | 20.6 | 16.6 | 13.4 | 10.7 |  |  |  | 280 | 46.6667 | 37.8378 | 31.1111 | 25.4545 | 20.5882 | 16.4706 | 13.3333 | 10.7692 |  |  | 280 | -0.3571% | 1.221% | 0.6071% | -0.2143% | 0.05714% | 0.7857% | 0.5% | -0.6429%
Yes | 315 | 52.3 | 43.1 | 35.2 | 28.6 | 23.2 | 18.7 | 15 | 12.1 | 9.7 | 7.7 |  | 315 | 52.5 | 42.5676 | 35 | 28.6364 | 23.1618 | 18.5294 | 15 | 12.1154 | 9.5455 | 7.6829 | 315 | -0.381% | 1.251% | 0.5714% | -0.127% | 0.1651% | 0.9206% | 0% | -0.127% | 1.619% | 0.2222%
Yes | 355 | 59 | 48.5 | 39.7 | 32.2 | 26.1 | 21.1 | 16.9 | 13.6 | 10.9 | 8.7 |  | 355 | 59.1667 | 47.973 | 39.4444 | 32.2727 | 26.1029 | 20.8824 | 16.9048 | 13.6538 | 10.7576 | 8.6585 | 355 | -0.2817% | 1.099% | 0.6479% | -0.2254% | -0.01127% | 1.042% | -0.02817% | -0.3944% | 1.324% | 0.4789%
Yes | 400 |  | 54.7 | 44.7 | 36.3 | 29.4 | 23.7 | 19.1 | 15.3 | 12.3 | 9.8 |  | 400 |  | 54.0541 | 44.4444 | 36.3636 | 29.4118 | 23.5294 | 19.0476 | 15.3846 | 12.1212 | 9.7561 | 400 |  | 1.195% | 0.575% | -0.175% | -0.04% | 0.725% | 0.275% | -0.55% | 1.475% | 0.45%
No | 450 |  | 61.5 | 50.3 | 40.9 | 33.1 | 26.7 | 21.5 | 17.2 | 13.8 | 11 |  | 450 |  | 60.8108 | 50 | 40.9091 | 33.0882 | 26.4706 | 21.4286 | 17.3077 | 13.6364 | 10.9756 | 450 |  | 1.133% | 0.6% | -0.02222% | 0.03556% | 0.8667% | 0.3333% | -0.6222% | 1.2% | 0.2222%
Yes | 500 |  |  | 55.8 | 45.4 | 36.8 | 29.7 | 23.9 | 19.1 | 15.3 | 12.3 |  | 500 |  |  | 55.5556 | 45.4545 | 36.7647 | 29.4118 | 23.8095 | 19.2308 | 15.1515 | 12.1951 | 500 |  |  | 0.44% | -0.12% | 0.096% | 0.98% | 0.38% | -0.68% | 0.98% | 0.86%
Yes | 560 |  |  | 62.5 | 50.8 | 41.2 | 33.2 | 26.7 | 21.4 | 17.2 | 13.7 |  | 560 |  |  | 62.2222 | 50.9091 | 41.1765 | 32.9412 | 26.6667 | 21.5385 | 16.9697 | 13.6585 | 560 |  |  | 0.4464% | -0.2143% | 0.05714% | 0.7857% | 0.125% | -0.6429% | 1.357% | 0.3036%
Yes | 630 |  |  | 70.3 | 57.2 | 46.3 | 37.4 | 30 | 24.1 | 19.3 | 15.4 |  | 630 |  |  | 70 | 57.2727 | 46.3235 | 37.0588 | 30 | 24.2308 | 19.0909 | 15.3659 | 630 |  |  | 0.4286% | -0.127% | -0.05079% | 0.9206% | 0% | -0.5397% | 1.095% | 0.2222%
Yes | 710 |  |  | 79.3 | 64.5 | 52.2 | 42.1 | 33.9 | 27.2 | 21.8 | 17.4 |  | 710 |  |  | 78.8889 | 64.5455 | 52.2059 | 41.7647 | 33.8095 | 27.3077 | 21.5152 | 17.3171 | 710 |  |  | 0.5211% | -0.07042% | -0.01127% | 0.8028% | 0.2676% | -0.3944% | 1.324% | 0.4789%
Yes | 800 |  |  | 89.3 | 72.6 | 58.8 | 47.4 | 38.1 | 30.6 | 24.5 | 19.6 |  | 800 |  |  | 88.8889 | 72.7273 | 58.8235 | 47.0588 | 38.0952 | 30.7692 | 24.2424 | 19.5122 | 800 |  |  | 0.4625% | -0.175% | -0.04% | 0.725% | 0.0125% | -0.55% | 1.063% | 0.45%
No | 900 |  |  |  | 81.7 | 66.1 | 53.3 | 42.9 | 34.4 | 27.6 | 22 |  | 900 |  |  |  | 81.8182 | 66.1765 | 52.9412 | 42.8571 | 34.6154 | 27.2727 | 21.9512 | 900 |  |  |  | -0.1444% | -0.1156% | 0.6778% | 0.1% | -0.6222% | 1.2% | 0.2222%
Yes | 1000 |  |  |  | 90.8 | 73.5 | 59.3 | 47.7 | 38.2 | 30.6 | 24.5 |  | 1000 |  |  |  | 90.9091 | 73.5294 | 58.8235 | 47.619 | 38.4615 | 30.303 | 24.3902 | 1000 |  |  |  | -0.12% | -0.04% | 0.81% | 0.17% | -0.68% | 0.98% | 0.45%
No | 1200 |  |  |  |  | 88.2 | 71.1 | 57.2 | 45.9 | 36.7 | 29.4 |  | 1200 |  |  |  |  | 88.2353 | 70.5882 | 57.1429 | 46.1538 | 36.3636 | 29.2683 | 1200 |  |  |  |  | -0.04% | 0.725% | 0.1% | -0.55% | 0.925% | 0.45%
No | 1400 |  |  |  |  | 102.8 | 83 | 66.7 | 53.5 | 42.9 | 34.3 |  | 1400 |  |  |  |  | 102.9412 | 82.3529 | 66.6667 | 53.8462 | 42.4242 | 34.1463 | 1400 |  |  |  |  | -0.1371% | 0.7857% | 0.05% | -0.6429% | 1.121% | 0.45%
No | 1600 |  |  |  |  | 117.5 | 94.8 | 76.2 | 61.2 | 49 | 39.2 |  | 1600 |  |  |  |  | 117.6471 | 94.1176 | 76.1905 | 61.5385 | 48.4848 | 39.0244 | 1600 |  |  |  |  | -0.125% | 0.725% | 0.0125% | -0.55% | 1.063% | 0.45%
No | 1800 | [5 empty] | 106.6 | 85.8 | 68.8 | 55.1 | 44 |  | 1800 | [5 empty] | 105.8824 | 85.7143 | 69.2308 | 54.5455 | 43.9024 | 1800 | [5 empty] | 0.6778% | 0.1% | -0.6222% | 1.017% | 0.2222%
No | 2000 | [5 empty] | 118.5 | 95.3 | 76.4 | 61.2 | 48.9 |  | 2000 | [5 empty] | 117.6471 | 95.2381 | 76.9231 | 60.6061 | 48.7805 | 2000 | [5 empty] | 0.725% | 0.065% | -0.68% | 0.98% | 0.245%
No | 2250 | [6 empty] | 107.2 | 86 | 68.9 | 55 |  | 2250 | [6 empty] | 107.1429 | 86.5385 | 68.1818 | 54.878 | 2250 | [6 empty] | 0.05333% | -0.6222% | 1.053% | 0.2222%
No | 2500 | [6 empty] | 119.1 | 95.5 | 76.5 | 61.2 |  | 2500 | [6 empty] | 119.0476 | 96.1538 | 75.7576 | 60.9756 | 2500 | [6 empty] | 0.044% | -0.68% | 0.98% | 0.368%
| SDR | 6 | 7.4 | 9 | 11 | 13.6 | 17 | 21 | 26 | 33 | 41
Size in WIS | Diameter | emax | emax | emax | emax | emax | emax | emax | emax | emax | emax
|  | 6emax | 7.4emax | 9emax | 11emax | 13.6emax | 17emax | 21emax | 26emax | 33emax | 41emax
No | 16 | 3.4 | 2.7 | 2.3
No | 20 | 3.9 | 3.4 | 2.7 | 2.3
No | 25 | 4.8 | 4 | 3.4 | 2.7 | 2.3
No | 32 | 6.1 | 5 | 4.1 | 3.4 | 2.8 | 2.3
No | 40 | 7.5 | 6.2 | 5.1 | 4.2 | 3.5 | 2.8 | 2.3
No | 50 | 9.3 | 7.7 | 6.3 | 5.2 | 4.2 | 3.4 | 2.8 | 2.3
Yes | 63 | 11.7 | 9.6 | 8 | 6.5 | 5.3 | 4.3 | 3.4 | 2.9
No | 75 | 13.9 | 11.5 | 9.4 | 7.6 | 6.3 | 5.1 | 4.1 | 3.3
Yes | 90 | 16.7 | 13.7 | 11.3 | 9.2 | 7.5 | 6.1 | 4.9 | 4
Yes | 110 | 20.3 | 16.8 | 13.7 | 11.1 | 9.1 | 7.4 | 6 | 4.8
Yes | 125 | 23 | 19 | 15.6 | 12.7 | 10.3 | 8.3 | 6.7 | 5.4
No | 140 | 25.8 | 21.3 | 17.4 | 14.1 | 11.5 | 9.3 | 7.5 | 6.1
Yes | 160 | 29.4 | 24.2 | 19.8 | 16.2 | 13.1 | 10.6 | 8.6 | 7
Yes | 180 | 33 | 27.2 | 22.3 | 18.2 | 14.8 | 11.9 | 9.6 | 7.7
No | 200 | 36.7 | 30.3 | 24.8 | 20.2 | 16.3 | 13.2 | 10.7 | 8.6
Yes | 225 | 41.3 | 34 | 27.9 | 22.7 | 18.4 | 14.9 | 12 | 9.6
Yes | 250 | 45.8 | 37.8 | 30.8 | 25.1 | 20.4 | 16.4 | 13.2 | 10.7
Yes | 280 | 51.3 | 42.3 | 34.6 | 28.1 | 22.8 | 18.4 | 14.9 | 11.9
Yes | 315 | 57.7 | 47.6 | 38.9 | 31.6 | 25.7 | 20.7 | 16.6 | 13.5 | 10.8 | 8.6
Yes | 355 | 65 | 53.5 | 43.8 | 35.6 | 28.9 | 23.4 | 18.7 | 15.1 | 12.1 | 9.7
Yes | 400 |  | 60.3 | 49.3 | 40.1 | 32.5 | 26.2 | 21.2 | 17 | 13.7 | 10.9
No | 450 |  | 67.8 | 55.5 | 45.1 | 36.6 | 29.5 | 23.8 | 19.1 | 15.3 | 12.2
Yes | 500 |  |  | 61.5 | 50.1 | 40.6 | 32.8 | 26.4 | 21.2 | 17 | 13.7
Yes | 560 |  |  | 68.9 | 56 | 45.5 | 36.7 | 29.5 | 23.7 | 19.1 | 15.2
Yes | 630 |  |  | 77.5 | 63.1 | 51.1 | 41.3 | 33.1 | 26.7 | 21.4 | 17.1
Yes | 710 |  |  | 87.4 | 71.1 | 57.6 | 46.5 | 37.4 | 30.1 | 24.1 | 19.3
Yes | 800 |  |  | 98.4 | 80 | 64.8 | 52.3 | 42.1 | 33.8 | 27.1 | 21.7
No | 900 |  |  |  | 90 | 72.9 | 58.8 | 47.3 | 38.3 | 30.5 | 24.3
Yes | 1000 |  |  |  | 100 | 80.9 | 65.4 | 52.6 | 42.2 | 33.5 | 27.1
No | 1200 |  |  |  |  | 97.2 | 78.4 | 63.1 | 50.6 | 40.5 | 32.5
No | 1400 |  |  |  |  | 113.3 | 91.5 | 73.5 | 59 | 47.3 | 37.9
No | 1600 |  |  |  |  | 129.4 | 104.4 | 84 | 67.5 | 54 | 43.3
No | 1800 | [5 empty] | 117.4 | 94.5 | 75.8 | 60.8 | 48.6
No | 2000 | [5 empty] | 130.4 | 105 | 84.2 | 67.5 | 53.9
No | 2250 | [6 empty] | 118.1 | 94.8 | 75.9 | 60.7
No | 2500 | [6 empty] | 131.2 | 105.2 | 84.3 | 67.5

## XX Minute,Modulus_Temp (hidden)
| Time | Material | Temperature (C) | Modulus (MPa)
| 0.01 | PE100 | 10 | 2160.5747 |  |  | y = 892.42x-0.192
| 0.1 | PE100 | 10 | 1388.5748
| 1 | PE100 | 10 | 892.42
| Time | Material | Temperature | Modulus
| 0.01 | PE100 | 20 | 1764.3021 |  |  | y = 606.14x-0.232
| 0.1 | PE100 | 20 | 1034.1248
| 1 | PE100 | 20 | 606.14
| 0.01 | PE80 | 20 | 1092.5113 |  |  | y = 407.78x-0.214
| 0.1 | PE80 | 20 | 667.461
| 1 | PE80 | 20 | 407.78
| Time | Material | Temperature | Modulus
| 0.01 | PE100 | 25 | 1487.9184 |  |  | y = 435.09x-0.267
| 0.1 | PE100 | 25 | 804.5983
| 1 | PE100 | 25 | 435.09
| 0.01 | PE80 | 25 | 919.1463 |  |  | y = 315.78x-0.232
| 0.1 | PE80 | 25 | 538.7467
| 1 | PE80 | 25 | 315.78
XX is: | Time (mins) | Time (h) | Material | Temperature (C) | Modulus (MPa) | Slope
30 | 30 | 0.5 | PE100 | 10 | 1019.4526 | 0.192
| 30 | 0.5 | PE100 | 20 | 711.8884 | 0.232
| 30 | 0.5 | PE100 | 25 | 523.5451 | 0.267
| 30 | 0.5 | PE80 | 20 | 472.9839 | 0.214
| 30 | 0.5 | PE80 | 25 | 370.8716 | 0.232

## DCLPE100 ModPerMinute (hidden)
Verification purposes
|  | PE100 | [5 empty] | Result of DCL Equation for
Min | Hours |  |  | PE100 Equation by DCL Graph |  |  |  | 10°C | 20 °C | 25°C
1 | 0.016667 | -43.338 | 2402.6 | Epe=2402.6-43.338T | 10 | 20 | 25 | 1969.22 | 1535.84 | 1319.15
2 | 0.033333 | -41.763 | 2141.6 | Epe=2141.6-41.763T | 10 | 20 | 25 | 1723.97 | 1306.34 | 1097.525
3 | 0.05 | -40.627 | 2001.2 | Epe=2001.2-40.627T | 10 | 20 | 25 | 1594.93 | 1188.66 | 985.525
4 | 0.066667 | -39.75 | 1906.6 | Epe=1906.6-39.75T | 10 | 20 | 25 | 1509.1 | 1111.6 | 912.85
5 | 0.083333 | -39.035 | 1836.2 | Epe=1836.2-39.035T | 10 | 20 | 25 | 1445.85 | 1055.5 | 860.325
6 | 0.1 | -38.434 | 1780.4 | Epe=1780.4-38.434T | 10 | 20 | 25 | 1396.06 | 1011.72 | 819.55
7 | 0.11667 | -37.914 | 1734.4 | Epe=1734.4-37.914T | 10 | 20 | 25 | 1355.26 | 976.12 | 786.55
8 | 0.13333 | -37.457 | 1695.5 | Epe=1695.5-37.457T | 10 | 20 | 25 | 1320.93 | 946.36 | 759.075
9 | 0.15 | -37.049 | 1661.9 | Epe=1661.9-37.049T | 10 | 20 | 25 | 1291.41 | 920.92 | 735.675
10 | 0.16667 | -36.681 | 1632.3 | Epe=1632.3-36.681T | 10 | 20 | 25 | 1265.49 | 898.68 | 715.275
11 | 0.18333 | -36.645 | 1605.9 | Epe=1605.9-36.645T | 10 | 20 | 25 | 1239.45 | 873 | 689.775
12 | 0.2 | -36.037 | 1582.2 | Epe=1582.2-36.037T | 10 | 20 | 25 | 1221.83 | 861.46 | 681.275
13 | 0.21667 | -35.752 | 1560.7 | Epe=1560.7-35.752T | 10 | 20 | 25 | 1203.18 | 845.66 | 666.9
14 | 0.23333 | -35.488 | 1541.1 | Epe=1541.1-35.488T | 10 | 20 | 25 | 1186.22 | 831.34 | 653.9
15 | 0.25 | -35.24 | 1523 | Epe=1523-35.24T | 10 | 20 | 25 | 1170.6 | 818.2 | 642
16 | 0.26667 | -35.008 | 1506.2 | Epe=1506.2-35.008T | 10 | 20 | 25 | 1156.12 | 806.04 | 631
17 | 0.28333 | -34.79 | 1490.6 | Epe=1490.6-34.79T | 10 | 20 | 25 | 1142.7 | 794.8 | 620.85
18 | 0.3 | -34.584 | 1476 | Epe=1476-34.584T | 10 | 20 | 25 | 1130.16 | 784.32 | 611.4
19 | 0.31667 | -34.389 | 1462.4 | Epe=1462.4-34.389T | 10 | 20 | 25 | 1118.51 | 774.62 | 602.675
20 | 0.33333 | -34.203 | 1449.6 | Epe=1449.6-34.203T | 10 | 20 | 25 | 1107.57 | 765.54 | 594.525
21 | 0.35 | -34.026 | 1437.4 | Epe=1437.4-34.026T | 10 | 20 | 25 | 1097.14 | 756.88 | 586.75
22 | 0.36667 | -33.858 | 1426 | Epe=1426-33.858T | 10 | 20 | 25 | 1087.42 | 748.84 | 579.55
23 | 0.38333 | -33.696 | 1415.1 | Epe=1415.1-33.696T | 10 | 20 | 25 | 1078.14 | 741.18 | 572.7
24 | 0.4 | -33.542 | 1404.8 | Epe=1404.8-33.542T | 10 | 20 | 25 | 1069.38 | 733.96 | 566.25
25 | 0.41667 | -33.394 | 1394.9 | Epe=1394.9-33.394T | 10 | 20 | 25 | 1060.96 | 727.02 | 560.05
26 | 0.43333 | -33.251 | 1385.5 | Epe=1385.5-33.251T | 10 | 20 | 25 | 1052.99 | 720.48 | 554.225
27 | 0.45 | -33.114 | 1376.5 | Epe=1376.5-33.114T | 10 | 20 | 25 | 1045.36 | 714.22 | 548.65
28 | 0.46667 | -32.982 | 1367.99 | Epe=1367.99-32.982T | 10 | 20 | 25 | 1038.17 | 708.35 | 543.44
29 | 0.48333 | -32.855 | 1359.6 | Epe=1359.6-32.855T | 10 | 20 | 25 | 1031.05 | 702.5 | 538.225
30 | 0.5 | -32.731 | 1351.7 | Epe=1351.7-32.731T | 10 | 20 | 25 | 1024.39 | 697.08 | 533.425
40 | 0.66667 | -31.687 | 1286.1 | y=-31.687x+1286.1 | 10 | 20 | 25 | 969.23 | 652.36 | 493.925
50 | 0.83333 | -30.879 | 1237.2 | y=-30.879x+1237.2 | 10 | 20 | 25 | 928.41 | 619.62 | 465.225
60 | 1 | -30.223 | 1198.6 | y=-30.223x+1198.6 | 10 | 20 | 25 | 896.37 | 594.14 | 443.025
PE100
For Modulus Calculation y=ax+b as per column Equations by DCL Graph
| a= | b= | y=
| -35.24 | 1523 | 1170.6 | This value is used for PE100
For Info Only
|  |  | 1164.5669 | AI Produced Equation calclulation

## DCLPE80 ModPerMinute (hidden)
Verification purposes
|  | PE80 | [5 empty] | Result of DCL Equation for
Min | Hours |  |  | PE80 Equation by DCL Graph |  |  |  | 10°C | 20 °C | 25°C
1 | 0.016667 | -32.591 | 1631.2 | Epe=1631.2-32.591T | 10 | 20 | 25 | 1305.29 | 979.38 | 816.425
2 | 0.033333 | -29.843 | 1441.2 | Epe=1441.2-29.843T | 10 | 20 | 25 | 1142.77 | 844.34 | 695.125
3 | 0.05 | -28.29 | 1340 | Epe=1340-28.29T | 10 | 20 | 25 | 1057.1 | 774.2 | 632.75
4 | 0.066667 | -27.16 | 1272.3 | Epe=1272.3-27.16T | 10 | 20 | 25 | 1000.7 | 729.1 | 593.3
5 | 0.083333 | -26.399 | 1222 | Epe=1222-26.399T | 10 | 20 | 25 | 958.01 | 694.02 | 562.025
6 | 0.1 | -25.743 | 1182.3 | Epe=1182.3-25.743T | 10 | 20 | 25 | 924.87 | 667.44 | 538.725
7 | 0.11667 | -25.196 | 1149.7 | Epe=1149.7-25.196T | 10 | 20 | 25 | 897.74 | 645.78 | 519.8
8 | 0.13333 | -24.729 | 1122.22 | Epe=1122.22-24.729T | 10 | 20 | 25 | 874.93 | 627.64 | 503.995
9 | 0.15 | -24.322 | 1098.4 | Epe=1098.4-24.322T | 10 | 20 | 25 | 855.18 | 611.96 | 490.35
10 | 0.16667 | -23.961 | 1077.6 | Epe=1077.6-23.961T | 10 | 20 | 25 | 837.99 | 598.38 | 478.575
11 | 0.18333 | -23.638 | 1059 | Epe=1059-23.638T | 10 | 20 | 25 | 822.62 | 586.24 | 468.05
12 | 0.2 | -23.346 | 1042.4 | Epe=1042.4-23.346T | 10 | 20 | 25 | 808.94 | 575.48 | 458.75
13 | 0.21667 | -23.079 | 1027.3 | Epe=1027.3-23.079T | 10 | 20 | 25 | 796.51 | 565.72 | 450.325
14 | 0.23333 | -22.834 | 1013.5 | Epe=1013.5-22.834T | 10 | 20 | 25 | 785.16 | 556.82 | 442.65
15 | 0.25 | -22.608 | 1000.8 | Epe=1000.8-22.608T | 10 | 20 | 25 | 774.72 | 548.64 | 435.6
16 | 0.26667 | -22.398 | 989.04 | Epe=989.04-22.398T | 10 | 20 | 25 | 765.06 | 541.08 | 429.09
17 | 0.28333 | -22.201 | 978.14 | Epe=978.14-22.201T | 10 | 20 | 25 | 756.13 | 534.12 | 423.115
18 | 0.3 | -22.017 | 967.97 | Epe=967.97-22.017T | 10 | 20 | 25 | 747.8 | 527.63 | 417.545
19 | 0.31667 | -21.844 | 958.44 | Epe=958.44-21.844T | 10 | 20 | 25 | 740 | 521.56 | 412.34
20 | 0.33333 | -21.681 | 949.8 | Epe=949.8-21.681T | 10 | 20 | 25 | 732.99 | 516.18 | 407.775
21 | 0.35 | -21.527 | 941.03 | Epe=941.03-21.527T | 10 | 20 | 25 | 725.76 | 510.49 | 402.855
22 | 0.36667 | -21.38 | 933.05 | Epe=933.05-21.38T | 10 | 20 | 25 | 719.25 | 505.45 | 398.55
23 | 0.38333 | -21.241 | 925.48 | Epe=925.48-21.241T | 10 | 20 | 25 | 713.07 | 500.66 | 394.455
24 | 0.4 | -21.108 | 918.28 | Epe=918.28-21.108T | 10 | 20 | 25 | 707.2 | 496.12 | 390.58
25 | 0.41667 | -20.981 | 911.43 | Epe=911.43-20.981T | 10 | 20 | 25 | 701.62 | 491.81 | 386.905
26 | 0.43333 | -20.86 | 904.9 | Epe=904.9-20.86T | 10 | 20 | 25 | 696.3 | 487.7 | 383.4
27 | 0.45 | -20.744 | 898.65 | Epe=898.65-20.744T | 10 | 20 | 25 | 691.21 | 483.77 | 380.05
28 | 0.46667 | -20.633 | 892.67 | Epe=892.67-20.633T | 10 | 20 | 25 | 686.34 | 480.01 | 376.845
29 | 0.48333 | -20.526 | 886.94 | Epe=886.94-20.526T | 10 | 20 | 25 | 681.68 | 476.42 | 373.79
30 | 0.5 | -20.422 | 881.43 | Epe=881.43-20.422T | 10 | 20 | 25 | 677.21 | 472.99 | 370.88
40 | 0.66667 | -19.563 | 836.01 | Epe=836.01-19.563T | 10 | 20 | 25 | 640.38 | 444.75 | 346.935
50 | 0.83333 | -18.916 | 802.33 | Epe=802.33-18.916T | 10 | 20 | 25 | 613.17 | 424.01 | 329.43
60 | 1 | -18.4 | 775.78 | Epe=775.78-18.4T | 10 | 20 | 25 | 591.78 | 407.78 | 315.78
PE80
For Modulus Calculation y=ax+b as per column Equations by DCL Graph
| a= | b= | y=
| -22.608 | 1000.8 | 774.72 | This values is used for PE80

## DCL Material Equations (hidden)
PE 100 | 1 Hour Modulus PE100 | Temp
y=-30.223x+1198.6 | 896.37 | 10
| 745.255 | 15
| 594.14 | 20
PE80
y=-18.4x+775.78 | 591.78 | 10
| 499.78 | 15
| 407.78 | 20

## SeveralNotes (hidden)
Temperature | Time (hours) | Expiremental equation |  | AI Equation result | Values from 1 hour Modulus equation | Rounding up AI
10 | 0.5 | EPE = 892.42t-0.192 | 1019.4526 | 1019.4517 | 896.37 | 1019.517
20 | 0.5 | EPE = 606.14t-0.232 | 711.8884 | 711.892 | 594.14 | 712.5215
25 | 0.5 | EPE = 435.09t-0.267 | 523.5451 | 523.5507 | 443.025 | 524.3033
Equations for Modulus
1 Hour PE Modulus PE80
Epe80 = 775.78 - (18.4*Temperature)
1 Hour PE Modulus PE100
Epe100 = 1198.6 - (30.223*Temperature)
Modulus of Water: 2,050,000,000 Pa

## Compare_Diff_StartP_same_DP (hidden)
| Table for Additional volume of water to raise the pressure for | [5 empty] | Table for Additional volume of water to raise the pressure for
| Material |  | PE100 |  |  |  | Material |  | PE100
| SDR |  | 17 |  |  |  | SDR |  | 17
| Length |  | 100 |  |  |  | Length |  | 100 |  |  |  | The table indicates how much less volume would be required if the starting pressure would be 5 instead of 1 , with the same increase of 10 bar
| Start Pressure (bar) |  | 1 |  |  |  | Start Pressure (bar) |  | 5
| Max Pressure (bar) |  | 11 |  |  |  | Max Pressure (bar) |  | 15
|  |  |  | Air % | [5 empty] | Air % |  |  |  |  | Air %
Diameter | 0 | 1 | 2 | 3 | 4 | 5 | 0 | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5
63 | 4.322 | 6.5133 | 8.7047 | 10.8961 | 13.0875 | 15.2788 | 4.322 | 5.929 | 7.536 | 9.143 | 10.75 | 12.357 | -0.58437 | -1.1687 | -1.7531 | -2.3375 | -2.9218
75 | 6.1341 | 9.2443 | 12.3544 | 15.4646 | 18.5748 | 21.685 | 6.1341 | 8.4149 | 10.6957 | 12.9765 | 15.2573 | 17.5381 | -0.82938 | -1.6588 | -2.4881 | -3.3175 | -4.1469
90 | 8.8331 | 13.3117 | 17.7904 | 22.269 | 26.7477 | 31.2264 | 8.8331 | 12.1174 | 15.4018 | 18.6861 | 21.9705 | 25.2548 | -1.1943 | -2.3886 | -3.5829 | -4.7772 | -5.9715
110 | 13.1951 | 19.8854 | 26.5758 | 33.2661 | 39.9564 | 46.6468 | 13.1951 | 18.1013 | 23.0076 | 27.9138 | 32.8201 | 37.7263 | -1.7841 | -3.5682 | -5.3523 | -7.1364 | -8.9204
125 | 17.1011 | 25.772 | 34.4428 | 43.1136 | 51.7844 | 60.4553 | 17.1011 | 23.4598 | 29.8184 | 36.177 | 42.5356 | 48.8942 | -2.3122 | -4.6244 | -6.9367 | -9.2489 | -11.5611
140 | 21.4433 | 32.3158 | 43.1882 | 54.0607 | 64.9331 | 75.8056 | 21.4433 | 29.4165 | 37.3896 | 45.3627 | 53.3359 | 61.309 | -2.8993 | -5.7986 | -8.698 | -11.5973 | -14.4966
160 | 27.9963 | 42.1913 | 56.3863 | 70.5813 | 84.7763 | 98.9713 | 27.9963 | 38.4059 | 48.8156 | 59.2253 | 69.6349 | 80.0446 | -3.7853 | -7.5707 | -11.356 | -15.1413 | -18.9267
180 | 35.4216 | 53.3815 | 71.3414 | 89.3013 | 107.2612 | 125.221 | 35.4216 | 48.5922 | 61.7628 | 74.9334 | 88.104 | 101.2745 | -4.7893 | -9.5786 | -14.3679 | -19.1572 | -23.9465
200 | 43.7194 | 65.8865 | 88.0536 | 110.2207 | 132.3878 | 154.5549 | 43.7194 | 59.9752 | 76.2311 | 92.487 | 108.7429 | 124.9988 | -5.9112 | -11.8225 | -17.7337 | -23.6449 | -29.5561
225 | 55.3184 | 83.3665 | 111.4147 | 139.4629 | 167.511 | 195.5592 | 55.3184 | 75.887 | 96.4557 | 117.0243 | 137.593 | 158.1617 | -7.4795 | -14.959 | -22.4385 | -29.918 | -37.3976
250 | 68.4046 | 103.0879 | 137.7712 | 172.4545 | 207.1378 | 241.8211 | 68.4046 | 93.839 | 119.2734 | 144.7078 | 170.1423 | 195.5767 | -9.2489 | -18.4978 | -27.7466 | -36.9955 | -46.2444
280 | 85.7734 | 129.2632 | 172.753 | 216.2428 | 259.7326 | 303.2224 | 85.7734 | 117.6659 | 149.5584 | 181.4509 | 213.3435 | 245.236 | -11.5973 | -23.1946 | -34.7918 | -46.3891 | -57.9864
315 | 108.5178 | 163.5398 | 218.5617 | 273.5837 | 328.6057 | 383.6276 | 108.5178 | 148.8672 | 189.2167 | 229.5661 | 269.9156 | 310.265 | -14.6725 | -29.345 | -44.0176 | -58.6901 | -73.3626
355 | 137.783 | 207.6433 | 277.5037 | 347.364 | 417.2243 | 487.0847 | 137.783 | 189.0139 | 240.2448 | 291.4757 | 342.7066 | 393.9375 | -18.6294 | -37.2588 | -55.8883 | -74.5177 | -93.1471
400 | 175.076 | 263.8451 | 352.6142 | 441.3833 | 530.1524 | 618.9215 | 175.076 | 240.1734 | 305.2707 | 370.368 | 435.4654 | 500.5627 | -23.6718 | -47.3435 | -71.0153 | -94.687 | -118.3588
450 | 221.4968 | 333.8027 | 446.1086 | 558.4145 | 670.7205 | 783.0264 | 221.4968 | 303.8545 | 386.2122 | 468.5698 | 550.9275 | 633.2852 | -29.9482 | -59.8965 | -89.8447 | -119.793 | -149.7412
500 | 273.3701 | 411.9774 | 550.5848 | 689.1921 | 827.7994 | 966.4067 | 273.3701 | 375.0155 | 476.6609 | 578.3062 | 679.9516 | 781.597 | -36.962 | -73.9239 | -110.8859 | -147.8478 | -184.8098
560 | 343.0934 | 517.0526 | 691.0119 | 864.9711 | 1038.9304 | 1212.8896 | 343.0934 | 470.6635 | 598.2336 | 725.8037 | 853.3738 | 980.9439 | -46.3891 | -92.7783 | -139.1674 | -185.5565 | -231.9457
630 | 434.0712 | 654.1591 | 874.247 | 1094.3348 | 1314.4227 | 1534.5106 | 434.0712 | 595.469 | 756.8668 | 918.2645 | 1079.6623 | 1241.0601 | -58.6901 | -117.3802 | -176.0703 | -234.7604 | -293.4505
710 | 551.4843 | 831.1044 | 1110.7244 | 1390.3445 | 1669.9645 | 1949.5846 | 551.4843 | 756.539 | 961.5937 | 1166.6485 | 1371.7032 | 1576.7579 | -74.5653 | -149.1307 | -223.696 | -298.2614 | -372.8267
800 | 700.3041 | 1055.3805 | 1410.4569 | 1765.5333 | 2120.6097 | 2475.6861 | 700.3041 | 960.6935 | 1221.0828 | 1481.4722 | 1741.8615 | 2002.2509 | -94.687 | -189.3741 | -284.0611 | -378.7482 | -473.4352
900 | 886.4341 | 1335.8843 | 1785.3345 | 2234.7847 | 2684.2349 | 3133.6852 | 886.4341 | 1216.0309 | 1545.6277 | 1875.2246 | 2204.8214 | 2534.4182 | -119.8534 | -239.7068 | -359.5602 | -479.4136 | -599.2669
1000 | 1093.9769 | 1648.6579 | 2203.3389 | 2758.0199 | 3312.7009 | 3867.3819 | 1093.9769 | 1500.743 | 1907.509 | 2314.2751 | 2721.0412 | 3127.8072 | -147.9149 | -295.8299 | -443.7448 | -591.6597 | -739.5747
1200 | 1575.6842 | 2374.6061 | 3173.528 | 3972.4499 | 4771.3718 | 5570.2937 | 1575.6842 | 2161.5603 | 2747.4363 | 3333.3124 | 3919.1885 | 4505.0645 | -213.0458 | -426.0917 | -639.1375 | -852.1834 | -1065.2292
|  | 1.507 | 1.3364 | 1.2517 | 1.2011 | 1.1674 |  | 1.3718 | 1.271 | 1.2132 | 1.1758 | 1.1495

## WallThickness12201-2 (hidden)
12201-2 Wall Thickness
| S | 2.5 | 2.5 | 3.2 | 3.2 | 4 | 4 | 5 | 5 | 6.3 | 6.3 | 8 | 8 | 10 | 10 | 12.5 | 12.5 | 16 | 16 | 20 | 20
| SDR | 6 | 6 | 7.4 | 7.4 | 9 | 9 | 11 | 11 | 13.6 | 13.6 | 17 | 17 | 21 | 21 | 26 | 26 | 33 | 33 | 41 | 41
Size in WIS | Diameter | emin | emax | emin | emax | emin | emax | emin | emax | emin | emax | emin | emax | emin | emax | emin | emax | emin | emax | emin | emax
|  | 6emin | 6emax | 7.4emin | 7.4emax | 9emin | 9emax | 11emin | 11emax | 13.6emin | 13.6emax | 17emin | 17emax | 21emin | 21emax | 26emin | 26emax | 33emin | 33emax | 41emin | 41emax
No | 16 | 3 | 3.4 | 2.3 | 2.7 | 2 | 2.3
No | 20 | 3.4 | 3.9 | 3 | 3.4 | 2.3 | 2.7 | 2 | 2.3
No | 25 | 4.2 | 4.8 | 3.5 | 4 | 3 | 3.4 | 2.3 | 2.7 | 2 | 2.3
No | 32 | 5.4 | 6.1 | 4.4 | 5 | 3.6 | 4.1 | 3 | 3.4 | 2.4 | 2.8 | 2 | 2.3
No | 40 | 6.7 | 7.5 | 5.5 | 6.2 | 4.5 | 5.1 | 3.7 | 4.2 | 3 | 3.5 | 2.4 | 2.8 | 2 | 2.3
No | 50 | 8.3 | 9.3 | 6.9 | 7.7 | 5.6 | 6.3 | 4.6 | 5.2 | 3.7 | 4.2 | 3 | 3.4 | 2.4 | 2.8 | 2 | 2.3
Yes | 63 | 10.5 | 11.7 | 8.6 | 9.6 | 7.1 | 8 | 5.8 | 6.5 | 4.7 | 5.3 | 3.8 | 4.3 | 3 | 3.4 | 2.5 | 2.9
No | 75 | 12.5 | 13.9 | 10.3 | 11.5 | 8.4 | 9.4 | 6.8 | 7.6 | 5.6 | 6.3 | 4.5 | 5.1 | 3.6 | 4.1 | 2.9 | 3.3
Yes | 90 | 15 | 16.7 | 12.3 | 13.7 | 10.1 | 11.3 | 8.2 | 9.2 | 6.7 | 7.5 | 5.4 | 6.1 | 4.3 | 4.9 | 3.5 | 4
Yes | 110 | 18.3 | 20.3 | 15.1 | 16.8 | 12.3 | 13.7 | 10 | 11.1 | 8.1 | 9.1 | 6.6 | 7.4 | 5.3 | 6 | 4.2 | 4.8
Yes | 125 | 20.8 | 23 | 17.1 | 19 | 14 | 15.6 | 11.4 | 12.7 | 9.2 | 10.3 | 7.4 | 8.3 | 6 | 6.7 | 4.8 | 5.4
No | 140 | 23.3 | 25.8 | 19.2 | 21.3 | 15.7 | 17.4 | 12.7 | 14.1 | 10.3 | 11.5 | 8.3 | 9.3 | 6.7 | 7.5 | 5.4 | 6.1
Yes | 160 | 26.6 | 29.4 | 21.9 | 24.2 | 17.9 | 19.8 | 14.6 | 16.2 | 11.8 | 13.1 | 9.5 | 10.6 | 7.7 | 8.6 | 6.2 | 7
Yes | 180 | 29.9 | 33 | 24.6 | 27.2 | 20.1 | 22.3 | 16.4 | 18.2 | 13.3 | 14.8 | 10.7 | 11.9 | 8.6 | 9.6 | 6.9 | 7.7
No | 200 | 33.2 | 36.7 | 27.4 | 30.3 | 22.4 | 24.8 | 18.2 | 20.2 | 14.7 | 16.3 | 11.9 | 13.2 | 9.6 | 10.7 | 7.7 | 8.6
Yes | 225 | 37.4 | 41.3 | 30.8 | 34 | 25.2 | 27.9 | 20.5 | 22.7 | 16.6 | 18.4 | 13.4 | 14.9 | 10.8 | 12 | 8.6 | 9.6
Yes | 250 | 41.5 | 45.8 | 34.2 | 37.8 | 27.9 | 30.8 | 22.7 | 25.1 | 18.4 | 20.4 | 14.8 | 16.4 | 11.9 | 13.2 | 9.6 | 10.7
Yes | 280 | 46.5 | 51.3 | 38.3 | 42.3 | 31.3 | 34.6 | 25.4 | 28.1 | 20.6 | 22.8 | 16.6 | 18.4 | 13.4 | 14.9 | 10.7 | 11.9
Yes | 315 | 52.3 | 57.7 | 43.1 | 47.6 | 35.2 | 38.9 | 28.6 | 31.6 | 23.2 | 25.7 | 18.7 | 20.7 | 15 | 16.6 | 12.1 | 13.5 | 9.7 | 10.8 | 7.7 | 8.6
Yes | 355 | 59 | 65 | 48.5 | 53.5 | 39.7 | 43.8 | 32.2 | 35.6 | 26.1 | 28.9 | 21.1 | 23.4 | 16.9 | 18.7 | 13.6 | 15.1 | 10.9 | 12.1 | 8.7 | 9.7
Yes | 400 |  |  | 54.7 | 60.3 | 44.7 | 49.3 | 36.3 | 40.1 | 29.4 | 32.5 | 23.7 | 26.2 | 19.1 | 21.2 | 15.3 | 17 | 12.3 | 13.7 | 9.8 | 10.9
No | 450 |  |  | 61.5 | 67.8 | 50.3 | 55.5 | 40.9 | 45.1 | 33.1 | 36.6 | 26.7 | 29.5 | 21.5 | 23.8 | 17.2 | 19.1 | 13.8 | 15.3 | 11 | 12.2
Yes | 500 |  |  |  |  | 55.8 | 61.5 | 45.4 | 50.1 | 36.8 | 40.6 | 29.7 | 32.8 | 23.9 | 26.4 | 19.1 | 21.2 | 15.3 | 17 | 12.3 | 13.7
Yes | 560 |  |  |  |  | 62.5 | 68.9 | 50.8 | 56 | 41.2 | 45.5 | 33.2 | 36.7 | 26.7 | 29.5 | 21.4 | 23.7 | 17.2 | 19.1 | 13.7 | 15.2
Yes | 630 |  |  |  |  | 70.3 | 77.5 | 57.2 | 63.1 | 46.3 | 51.1 | 37.4 | 41.3 | 30 | 33.1 | 24.1 | 26.7 | 19.3 | 21.4 | 15.4 | 17.1
Yes | 710 |  |  |  |  | 79.3 | 87.4 | 64.5 | 71.1 | 52.2 | 57.6 | 42.1 | 46.5 | 33.9 | 37.4 | 27.2 | 30.1 | 21.8 | 24.1 | 17.4 | 19.3
Yes | 800 |  |  |  |  | 89.3 | 98.4 | 72.6 | 80 | 58.8 | 64.8 | 47.4 | 52.3 | 38.1 | 42.1 | 30.6 | 33.8 | 24.5 | 27.1 | 19.6 | 21.7
No | 900 | [6 empty] | 81.7 | 90 | 66.1 | 72.9 | 53.3 | 58.8 | 42.9 | 47.3 | 34.4 | 38.3 | 27.6 | 30.5 | 22 | 24.3
Yes | 1000 | [6 empty] | 90.8 | 100 | 73.5 | 80.9 | 59.3 | 65.4 | 47.7 | 52.6 | 38.2 | 42.2 | 30.6 | 33.5 | 24.5 | 27.1
No | 1200 | [8 empty] | 88.2 | 97.2 | 71.1 | 78.4 | 57.2 | 63.1 | 45.9 | 50.6 | 36.7 | 40.5 | 29.4 | 32.5
No | 1400 | [8 empty] | 102.8 | 113.3 | 83 | 91.5 | 66.7 | 73.5 | 53.5 | 59 | 42.9 | 47.3 | 34.3 | 37.9
No | 1600 | [8 empty] | 117.5 | 129.4 | 94.8 | 104.4 | 76.2 | 84 | 61.2 | 67.5 | 49 | 54 | 39.2 | 43.3
No | 1800 | [10 empty] | 106.6 | 117.4 | 85.8 | 94.5 | 68.8 | 75.8 | 55.1 | 60.8 | 44 | 48.6
No | 2000 | [10 empty] | 118.5 | 130.4 | 95.3 | 105 | 76.4 | 84.2 | 61.2 | 67.5 | 48.9 | 53.9
No | 2250 | [12 empty] | 107.2 | 118.1 | 86 | 94.8 | 68.9 | 75.9 | 55 | 60.7
No | 2500 | [12 empty] | 119.1 | 131.2 | 95.5 | 105.2 | 76.5 | 84.3 | 61.2 | 67.5

## PE 80-100 MInMaxSDRWall (hidden)
Pipe Diameter (mm) | 63
SDR | 17
PE80 or PE100 | PE100
Length (m) | 1000
Percent air | 1%
Start Pressure (bar) (absolute) | 1
Max Pressure (bar) (absolute) | 11
delta P (Pa) | 1000000
Pipe Radius (meters) | 0.0315
Pipe WallThickness(meters)/SDR | 0.0037059
Pipe WallThickness(meters)/Min | 0.0038
Pipe WallThickness(meters)/Max | 0.0043
E (Pa) | 860000000
modulus of water | 2050000000 |  | 0.96422
| Calc based on Min Wall Thickness | Calc based on Max Wall Thickness | Calc based on SDR Wall Thickness
Pipe Volume(liters) | 2410.5126 | 2324.2759 | 2426.9211
Pressurisation Volume (No Air) | 43.2197 | 41.6735 | 43.5139
Pressurisation Volume with 1% air | 65.1334 | 62.8033 | 65.5768
Table for additional volume of water to raise the pressure for: (min wall thickness)
| Material | PE100
| SDR | 17
| Length | 100
| Start Pressure (bar) | 1
| Max Pressure (bar) | 11
Air %
Diameter | 0 | 1 | 2 | 3 | 4 | 5 | Pipe Volume (l) Min Wall Thickness
63 | 43.2197 | 65.1334 | 87.0472 | 108.9609 | 130.8747 | 152.7884 | 2410.5126
75 | 61.3409 | 92.4426 | 123.5444 | 154.6462 | 185.7479 | 216.8497 | 3421.1944
90 | 88.3309 | 133.1174 | 177.9039 | 222.6905 | 267.477 | 312.2636 | 4926.5199
110 | 131.951 | 198.8544 | 265.7577 | 332.6611 | 399.5645 | 466.4678 | 7359.3693
125 | 171.0115 | 257.7197 | 344.428 | 431.1362 | 517.8444 | 604.5527 | 9537.9067
140 | 214.4334 | 323.1579 | 431.8824 | 540.6069 | 649.3315 | 758.056 | 11959.6977
160 | 279.9628 | 421.9128 | 563.8628 | 705.8128 | 847.7628 | 989.7128 | 15614.5009
180 | 354.2162 | 533.8151 | 713.4139 | 893.0128 | 1072.6116 | 1252.2105 | 19755.874
200 | 437.1937 | 658.8647 | 880.5358 | 1102.2069 | 1323.8779 | 1545.549 | 24383.817
225 | 553.1837 | 833.6654 | 1114.147 | 1394.6287 | 1675.1104 | 1955.5921 | 30852.9845
250 | 684.0459 | 1030.8789 | 1377.7118 | 1724.5448 | 2071.3778 | 2418.2108 | 38151.6268
280 | 857.7335 | 1292.6316 | 1727.5297 | 2162.4278 | 2597.3259 | 3032.224 | 47838.7906
315 | 1085.178 | 1635.3977 | 2185.6174 | 2735.8371 | 3286.0567 | 3836.2764 | 60524.1648
355 | 1377.8297 | 2076.4331 | 2775.0365 | 3473.6399 | 4172.2433 | 4870.8467 | 76846.3722
400 | 1750.7603 | 2638.4513 | 3526.1422 | 4413.8332 | 5301.5242 | 6189.2152 | 97646.009
450 | 2214.9681 | 3338.0273 | 4461.0864 | 5584.1455 | 6707.2046 | 7830.2637 | 123536.5023
500 | 2733.7012 | 4119.7745 | 5505.8477 | 6891.921 | 8277.9942 | 9664.0675 | 152468.0574
560 | 3430.934 | 5170.5264 | 6910.1188 | 8649.7112 | 10389.3036 | 12128.896 | 191355.1625
630 | 4340.7121 | 6541.5908 | 8742.4695 | 10943.3482 | 13144.227 | 15345.1057 | 242096.6591
710 | 5514.8434 | 8311.0439 | 11107.2444 | 13903.445 | 16699.6455 | 19495.846 | 307582.0584
800 | 7003.0411 | 10553.805 | 14104.569 | 17655.3329 | 21206.0969 | 24756.8609 | 390584.0359
900 | 8864.3411 | 13358.8432 | 17853.3453 | 22347.8474 | 26842.3495 | 31336.8516 | 494395.2319
1000 | 10939.7691 | 16486.5791 | 22033.3891 | 27580.1991 | 33127.0091 | 38673.8191 | 610149.0982
1200 | 15756.8424 | 23746.0613 | 31735.2802 | 39724.4991 | 47713.718 | 55702.9369 | 878814.0807
Draft